## Slide 1: Controls Issues Injection beam2 test meeting 28th Aug 2008
Eugenia Hatziangeli
Input from J. Lewis, M. Sobzak, JJ Gras, C. Roderick, M.Pace, N. Stapley, P. Charrue, G. Kruk, A. Bland, M. Arruat,
E. Hatziangeli

## Slide 2: Timing
Several problems at the same time
Mismatch between the tables loaded in the master LHC MTG and the ones in the Operational application
  Unable to load injection timing table
    Error possibly due to timeout
    Julian is working on a fix on the task server on the MTGS to avoid incoherent tables being loaded
CRT LTIM was disabled
  Timing events were not coming out
  Test LTIM that triggers every SPS extraction was enabled by mistake
  Test LTIM is now suppressed which was killing the TI8/TI2 LTIMs output
Payload was set to 0xFFFF
  Timing events were coming out on every cycle not just LHC
  Test LTIM that triggers every SPS extraction was enabled by mistake forcing the payload to 0xFFFF
E. Hatziangeli Injection beam2 test meeting report 28th Aug 2008

## Slide 3: FESA Servers
Several bugs on CMW (RDA) and FESA were corrected prior to the Beam 2 test
Servers reporting crashes, [BI servers (BLM, BPM), XTIM] were relinked with the new version 1 week prior to test and were put under automatic restart if crash
  No crash was observed during that week [BI made several stress tests and crashes were not induced]
Friday PM # of clients increased => XTIM server unable to serve
    Increase buffer resolved situation
XTIM Instability was recorded during the weekend (crash/blockage)
BLM, BPM instabilities (several crashes) during the weekend recorded
Investigation into RDA revealed a weakness which can lead to server crash
Fix was released. XTIM is being tested with this now, BI follows
E. Hatziangeli Injection beam2 test meeting report 28th Aug 2008

## Slide 4: Logging
General logging was stable no holes in data
LHC Collimators logging restricted to sectors 7-8 and 2-3
  Full LHC collimator logging load was tested during the days before => no problem but WITHOUT the full data load from other parameters (all XPOC-event triggered data) enabled
BPM logging - small hickups but nothing major
BLM logging
  Started with logging sectors 7-8 and 2-3 together
  Several holes of data were observed
  Bottleneck in the database client API
    Switched to sector 7-8 on Saturday
  An improved version of the API was delivered on Sunday AM (parallelization in place)
    Sectors 7-8 and 2-3 were logged since then with no interruption/data loss
  Stress tests with all BLMs logged will be started tomorrow
New version of the API will be used in all our logging clients
E. Hatziangeli Injection beam2 test meeting report 28th Aug 2008

## Slide 5: Some Numbers
JMS
60-70 client connections
18-20 CCC consoles
40-45 CCR servers
3 - 5 office or cernts
370-400 subscriptions
Network traffic
  Input: 2-4MB/s
  Output 10-30MB/s
Both input and output were highest evening and overnight Sunday-Monday (24th-25th).
Message counts < 3 million per day
Disk Usage – SDDS Logging
      Size Used Avail Use%
sps_data 493G 242G 226G 52%
lhc_data 493G 149G 319G 32%
The beam2 test produced
  15Gbytes on SPS (33 GBytes beam1)
  3Gbytes on LHC (17 GBytes beam1)
Remaining 500G + 500G on order
Meas DB in MBytes

## Slide 6: RBAC
RBAC settings during the test:
  RBAC-enable = true
  RBAC-policy = no check (lenient, strict)
FESA servers 2.10 and PO
  RBACed client applications sending RBAC token to the server, the token will be ignored, the call will work as before
  NonRBACed client applications will work as before
FESA servers 2.9 with RBAC rules applied the previous default policy (lenient) => correct role is needed
New FESA 2.9 framework with present RBAC functionality is now available
  BT will move to this
  RF, collimators to be decided
OP-RBAC responsible has provided a list of all OP applications to be RBAC enabled
  Component to manage RBAC token in GUIs is available
10th Sept proposal
  All required application should be RBAC enabled
  RBAC-policy = lenient
    No token - grant
    Get without rules - grant
    Get with rules - check rules
    Set without rules - grant
    Set with rules - check rule
  Slot in dry runs before the 10th September
E. Hatziangeli Injection beam2 test meeting report 28th Aug 2008

## Slide 7: Summary
Several Issues with the Timing on Friday
  Once understood the recovery was quick
  Fixes are on the way
FESA/CMW servers for BI and XTIM became unstable during the weekend (high # of clients connections?)
  CMW fix is already deployed – under test
Logging - no loss of data, also for the BLM once the improved API was deployed
  Testing for all the ring and use new API everywhere
RBAC behaved as expected => no interference with the test
  RBAC enable all appropriate applications, dry tests and go for the lenient policy for the 10th September
E. Hatziangeli Injection beam2 test meeting report 28th Aug 2008